## Slide 1: Everett Water Supply Resiliency
Souheil Nasr, P.E.
Everett Public Works
March 25, 2019

## Slide 2: Resiliency Parameters
Critical/essential facilities
Designed to resist earthquakes with 2% chance in 50 years
Equivalent to Mw7.4 SWIF earthquake

## Slide 3: Earthquakes Considered
Mw9.0 CSZ, PGA 18-34 %g
Mw7.4 SWIF, PGA 65-124 %g
Mw7.4 SWIF is 3 – 4 times more violent than Mw9.0 CSZ
Cascadia Earthquake
South Whidbey Island Fault

## Slide 4: Importance Post-EQ Water Supply
Public health
Fire fighting
Economic continuity

## Slide 5: Everett Earthquake Likelihood
In next 50 years (USGS):
  14% chance of Mw9.0 CSZ
  15% chance of Mw6.5+ surface fault
  85% chance >1 deep earthquake

## Slide 6: Everett Water Supply System

## Slide 7: Resiliency Project Findings
Mw7.4 SWIF earthquake:
  Res 2 complete damage
  Res 3 & 6 extensive damage
  Chaplain N&S dams extensive damage
  WFP moderate damage
  20+ breaks/leaks in TLs

## Slide 8: Economic Cost
  WFP building extensive damage
  WPCF moderate damage
  20+ breaks and leaks
  Clearview reservoir extensive damage
  30+ breaks/leaks in Clearview line

## Slide 9: Everett Seismic Mitigation
TLs 2 & 3 - 2009
Pile-supported TL 5 - 2010
Water supply risk assessment - 2012
WFP OP bldg. seismic retrofit - 2017

## Slide 10: Everett Seismic Mitigation
Resiliency study – 2016/2018
Distribution main replacement with earthquake resistant pipe - now
Replace Res 2 – in design

## Slide 11: Short Term (10 Yrs)Mitigation Plan
Enhance preparedness & response
  Finalize earthquake response plan
  Augment TL repair material stocks
  Assess emergency drinking water
Implement resiliency CIP program Totaling $94 Million over 10 Yrs

## Slide 12: Short Term (10 Yrs) Mitigation Plan
Implement water isolation strategies
  Isolation valves at Res 2, 3 & 6
  EQ resistant distribution system
  Add strategic valves for isolating
Keep Res 4 as non-potable storage

## Slide 13: Water Supply Recovery Curves
Mw9.0 CSZ earthquake
  PGAs <0.2 in Everett’s system
  Reservoir 2 complete damage
  Up to 15 breaks & leaks

## Slide 14: Long Term (50 Yrs) Mitigation Plan
Backbone Distribution System
  Use earthquake resistant pipe
  Implement isolation strategy
Upgrade/replace vulnerable facilities
  Reservoirs 3, 6
  Key pump stations & support facilities

## Slide 15: Everett Water Backbone System

## Slide 16: Summary
Seismic planning is a long term priority
Seismic projects are in the water CIP
Seismic planning is a city-wide effort

## Slide 17
Questions?